## Lot 1 5 kVA 50 Hz
Company Name:
Make and model:
Lot 1, 5kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 5 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state →
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
Emisson norms: EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or other, if any. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 2 10 kVA 50 HZ
Company name:
Make and model:
Lot 2, 10kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 10 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state →
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 3 20 kVA 50 Hz
Company Name:
Make and model:
Lot 3, 20kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 20 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 4 30 kVA 50 Hz
Company name:
Make and model:
Lot 4, 30kVA 50Hz
GENERATOR SET SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 30 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 5 40 kVA 50 Hz
Company Name:
Make and model:
Lot 5, 40kVA 50 Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 40 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 6 60 kVA 50 Hz
Company name:
Make and model:
Lot 6, 60kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 60 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 7 80 kVA 50 Hz
Company name:
Make and model:
Lot 7, 80kVA 50 Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 80 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 8 100 kVA 50 Hz
Company name:
Make and model:
Lot 8, 100kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 100 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 9 150 kVA 50 Hz
Company name:
Make and model:
Lot 9, 150kVA 50hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 150 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 10 200 kVA 50 Hz
Company name:
Make and model:
Lot 10, 200kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 200 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 11 300 kVA 50 Hz
Company Name:
Make and model:
Lot 11, 300kVA 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 300 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 12 500 kVA 50 Hz
Company name:
Make and model:
Lot 12, 500kVa 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 500 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 13 700 kVA 50 Hz
Company name:
Make and model:
Lot 13, 700kVa 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 700 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 14 1000 kVa 50 Hz
Company name:
Make and model:
Lot 14, 1000 kVa 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 1000 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V, other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 15 1500 kVa 50 Hz
Company name:
Make and model:
Lot 15, 1500 kVa 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 1500 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V, other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 16 2000 kVa 50 Hz
Company name:
Make and model:
Lot 16, 2000 kVa 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 2000 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V, other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 50 Hz | Comply →
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 17 5 kVA 60 Hz
Company name:
Make and model:
Lot 17, 5VA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 5 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 18 10 kVA 60 Hz
Company name:
Make and model:
Lot 18, 10kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 10 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 19 20 kVA 60 Hz
Company name:
Make and model:
Lot 19, 20kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 20 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 20 30 kVa 60 Hz
Company name:
Make and model:
Lot 20, 30kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 30 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 21 40 kVA 60 Hz
Company name:
Make and model:
Lot 21, 40kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 40 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 22 60 kVA 60 Hz
Company name:
Make and model:
Lot 22, 60 kVA 60 HZ
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 60 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 23 80 kVA 60 Hz
Company name:
Make and model:
Lot 23, 80 kVA 60 Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 80 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 24 100 kVA 60 Hz
Company name:
Make and model:
Lot 24, 100kVA 60 Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 100 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 25 150 kVA 60 Hz
Company name:
Make and model:
Lot 25 150 kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 150 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 26 200 kVA 60 Hz
Company name:
Make and model:
Lot 26, 200 kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 200 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 27 300 kVA 60 Hz
Company name:
Make and model:
Lot 27, 300kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 300 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 28 500 kVA 60 Hz
Company name:
Make and model:
Lot 28, 500kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 500 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 29 700 kVA 60 Hz
Company Name:
Make and model:
Lot 29, 700kVA 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 700 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 120/210 V or other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 30 1000 kVa 60 Hz
Company name:
Make and model:
Lot 30, 1000 kVa 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 1000 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V, other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 31 1500 kVa 60 Hz
Company name:
Make and model:
Lot 31, 1500 kVa 60Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 1500 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V , other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→

## Lot 32 2000 kVa 60 Hz
Company name:
Make and model:
Lot 32, 2000 kVa 50Hz
GENERATOR SET SPECS | OUR REQUIREMENT | YOUR TECHNICAL OFFER
Complete generator set for autonomous operation, including diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories for autonomous operation. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply →
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
Rated power output, min. 2000 kVA | Comply and state →
Power factor: 0.8 or other | Please state →
Rated power, kW | Please state →
Voltage, 220/230/240 and/or 380/400 V, other | Please state →
Phase: 1 or 3 | Please state →
Output: A | Please state →
AC frequency, 60 Hz | Comply →
Speed: rpm 1800 or 3600 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply →
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply →
Derating information (temperature, altitude and humidity), please state | Please state →
ENGINE
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply →
Type: 4-stroke | Comply →
Injection: Indirect, direct, other | Please state →
Aspiration: Normal or turbo or turbo with inter cooler | Please state →
Cylinders, numbers: | Please state →
Configuration, inline, V, opposed flat, other | Please state →
Displacement, cc | Please state →
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Air filter | Comply →
Fuel filter | Comply →
Oil filter | Comply →
Exhaust with suitable piping and residential silencer | Comply →
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissons at 75% load: g/hour | Please state →
ALTERNATOR
Make: | Please state →
Model: | Please state →
Brushless type | Comply →
Cooling, please state: | Please state →
Protection class min. IP 23 | Comply →
Suitable AC power outlets protected by circuit breaker (state type) | Comply →
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply →
Voltage regulator | Comply →
STANDARD ACCESSORIES
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→
Low oil pressure protection, automatic shut down | Comply →
Over heating protection | Comply →
Overload protection | Comply →
Emergency stop | Comply →
Electric starter with key and battery | Comply →
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply →
Earthing facility | Comply →
Mounted on anti-vibration mounts | Comply →
Lifting points for handling | Comply →
Installation instructions and evt. drawings, English/French/Spanish | Comply →
Operators and maintenance manual, English/French/Spanish | Comply →
Tool kit | Comply →
Basic maintenance kit: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply →
Dimensions, L x W x H, mm | Please state →
Weight, dry: kg: | Please state →
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Nonroad and stationary emissions reagulations to Tier 1,2,3,4 or equivalent. Please state. | Please state →
OPTIONS
Spare parts & maintenance kit for min. 2500 hours of operation | Please provide price or state STD→
Heavy duty air filter for dusty conditions | Please provide price or state STD→
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→
High chimney for exhaust, state height and materials | Please provide price or state STD→
(ATS) Automatic Transfer Switch | Please provide price or state STD→
Over speed protection | Please provide price or state STD→
Manual transfer switch | Please provide price or state STD→
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Please provide price or state STD→
Slow moving trolley/trailer | Please provide price or state STD→
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→
Automatic main circuit breaker | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. | Please provide price or state STD→
Equipment for this diesel generator set to work in conjunction with a Photo Voltaic (PV) system with battery back-up. Device to measure charge level of PV battery and Device to start the diesel generator set upon reaching a predefined level of discharge of the battery in order to take over electricity supply for the loads. And to stop the diesel generator set when state of charge has reached a predefined level. In addition facility to allow diesel generator set to charge PV back-up battery. | Please provide price or state STD→
Work shop manual | Please provide price or state STD→
Spare parts catalogue | Please provide price or state STD→
Operators and maintenance manual, other languages | Please provide price or state STD→